## Foglio1
Oxygen cylinder
Published on: 19 November 2020 - Version: 2
Version 1: September 2019 (WHO-UNICEF)
Technical Specification | Minimum requirements
General technical requirements | Oxygen and medical air cylinders are refillable containers for such gas, in a compressed form, available in international standard capacity/pressure and dimensions. The cylinders can be made of steel, aluminium/alloy, carbon fibre or other composite material. Nominal pressure should be 13 700 kPa (137 bar, 1987 psi) for standard cylinders and 23 000 or 30 000 kPa (230 or 300 bar, 3336 or 4351 psi) for cylinders fitted with integral valves. Each cylinder is fitted and supplied with a valve. Multiple options for pressure regulators, various fitting and outlets, and integral valves should be available separately. Specific ISO, American National Standards Institute (ANSI) and other international colour coding for oxygen and medical air should be available. Accessories like holders, racks and trolleys should be available separately. Oxygen cylinders: • Refillable cylinders for compressed oxygen (oil-free and compliant to ISO standards) or air (compliant to ISO standards) for medical use. • Fitted with a primary valve, standard (pin index or bullnose) or integral, refillable. • Nominal pressure 13 700 kPa (137 bar, 1987 psi), for standard valve cylinders, or 23 000–30 000 kPa (230–300 bar, 3336–4351 psi) depending on the cylinder model, for integral valve cylinders. • Compressed Gas Association (CGA) approved seamless steel/aluminium alloy/composite body, colour coding according to ISO/ANSI/CGA/NFPA, sizes ISO/US standard. • Cylinders supplied with optional pressure regulators, multiple fitting according to all the international standards. • Safety over-pressure release valve (if not built-in in the integral valve fitted cylinders). Primary valve and pressure regulator assemblies: • Pin index or bullnose primary valve and compatible pressure regulators, providing pressure regulated supply of oxygen (oil-free and compliant to ISO standards) or medical air (compliant to ISO standards). • Steel/plated brass/aluminium casing, brass valve. • Pin index and bullnose primary valve versions, handle/key operated, supplied with tools. • Nominal inlet pressure 13 700 kPa (137 bar, 1987 psi), maximum 20 000 kPa (200 bar, 2901 psi). • Outlet pressure 345 kPa (3.5 bar, 50 psi). • Integrated manometer, 0–20 000 kPa (0–200 bar, 0–2901 psi). • Safety over-pressure release valve. • Pressure regulator supplied with flowmeter, if required – see configurations/options for specifications. Integral valves: • All-in-one cylinder valve for oxygen (oil-free and compliant to ISO standards) or medical air (compliant to ISO standards), providing direct attachment to the cylinder, pressure regulation and supply of medical gas with adjustable flow rate. • Steel/plated brass/aluminium casing, brass valve. • 6 mm barbed and BS 5682 Schrader (if applicable depending on the size of the cylinder) outlets. • Integrated open/close valve, outlet nominal pressure 400 kPa (4 bar, 58 psi). • Inlet pressure 23 000–30 000 kPa (230–300 bar, 3336–4351 psi), depending on the cylinder model. • Integrated refill valve ISO 5145/CGA 540 compliant. • Integrated manometer, covering the full nominal pressure range of the cylinder, standard 23 000–30 000 kPa (230–300 bar, 3336–4351 psi), for integral valve cylinders, or whatever applicable. • Integrated flowmeter. • Safety over-pressure release valve. Capable of being stored in ambient temperature of at least 5–50 °C, relative humidity of at least 15–95% non-condensing. Suitable for continuous operation in ambient temperature of at least 5–45 °C, relative humidity of at least 15–90% non-condensing. Specific requirements for altitude may be required, depending on the installation site. Applicable regulations on transport and storage of cylinders may vary if the cylinders are empty or partially/fully filled. Compliance with regulations on hazardous goods, flammable, explosive, compressed gas, according to the Globally Harmonized System of Classification and Labelling of Chemicals (GHS) and international standards, is mandatory.
Configurations/Options | Oxygen cylinder configurations/versions/options: Standard and MRI-compatible versions. Specific ISO/ANSI/CGA/NFPA colour coding for oxygen and medical air. Seamless cylinders made of steel, aluminium/alloy, carbon fibre or other composite material (CGA approved and compliant to ISO applicable standards). Pin index/bullnose and integral valve options. OXYGEN and MEDICAL AIR cylinders with STANDARD VALVE available in all the ISO international standard sizes, including size AZ, C, D, E, F, G, H, J, and also US sizes M2 to M 265 (not all sizes apply to both oxygen and medical air). The type of standard valve has to be compliant to international ISO and US standards, i.e. pin index ISO 407/BS 850/CGA 870 valve, CGA 540 valve, 5/8 inch BSP (F) Bullnose BS 341 valve, also according to the size/pressure of the cylinder and to any applicable regulation. OXYGEN cylinders should be available also with INTEGRAL VALVE (with manometer and flow regulator, 400 kPa (4 bar) nominal outlet pressure, 6 mm barbed and BS 5682 Schrader outlets), in all the ISO international standard sizes, including size ZA, CD, ZD, HX and ZX, and also US sizes in M coding system. Regulator/integral valve configurations/versions: Standard and MRI-compatible versions. Oxygen and medical air versions. Pressure regulators and integral valves should be available with DISS and 6 mm barbed outlet. Pressure regulators should be available in basic open/close model and fitted with integrated flowmeter, Thorpe tube or Bourdon gauge. Pressure regulators and integral valves with Thorpe or Bourdon flowmeter should be available at least in the following flow ranges, for oxygen and medical air: • Low flow 0–3 or 4 L/min (only for oxygen), discrete (dial) flow setting (indicative steps 0, 0.03, 0.06, 0.12, 0.25, 0.50, 0.75, 1.0, 1.5, 2.0, 3.0, 4.0), accuracy 10%. • Standard flow 0–15 L/min, discrete (dial) flow setting (indicative steps 0, 0.25, 0.5, 1.0, 2.0, 3.0, 4.0, 5.0, 6.0, 8.0, 10.0, 12.0, 15.0), accuracy 10%. • High flow 0–25 L/min minimum, discrete (dial) flow setting (indicative steps 0, 0.25, 0.50, 1.0, 2.0, 3.0, 4.0, 6.0, 8.0, 10.0, 15.0, 25.0), accuracy 10%. Pressure regulators and integral valves with Thorpe or Bourdon flowmeter should be available at least in the following flow ranges, for oxygen and medical air: • Low flow 0–3 or 4 L/min (only for oxygen), accuracy 10%, indicative graduation (L/min) 0.03, 0.06, 0.12, 0.25, 0.5, 0.75, 1.0, 1.5, 2.0, 3.0, 4.0. • Standard flow 0–7 or 8 and 0–15 or 16 L/min, accuracy 10%, graduation 0.5 L/min (0.5–3 range) and 1 L/min (3–max range). • High flow 0–25 L/min minimum, accuracy 10%, graduation 0.5 L/min first increment and 1 L/min full range. Cylinder body, primary valve and pressure regulator or integral valve assembly, outlet connectors, safety pressure release valve, valve/regulator knob, manometer and flowmeter (for integral valve). Portable or stationary (depending on the size of the cylinder). Brass valve assemblies. Cylinders made of steel, aluminium/alloy, carbon fibre or compound material. Bronze/brass/synthetic sealings. All materials in contact with air certified for medical use.
Displayed parameters | Pressure and flow (for integral valve cylinders only).
User adjustable settings | Open/close control, pressure and flow (for integral valve cylinders only).
Accessories | Cylinder holding, carts, trolleys. Supplied with keys and tools to operate valves and regulators. Complete set of tubing and adapters to use the pressure regulator and the integral valve with all common international standard fittings, for medical gas sources, patient circuits and other medical devices.
Spare parts | Common and frequently used spare parts, sensors/transducers/actuators, reusable probes/cables/patient connection accessories, periodic maintenance and calibration kits/materials, renewables that should be procured together with the equipment and in quantity sufficient for 2 years recommended (1 year at least) of typical use. These items should be supplied to each department where the equipment is installed and also to central and local maintenance department. Sealing set, maintenance kit, regulating unit (knob), adapters and connectors, keys and tools to operate the valves. Items in the above-mentioned categories that are not frequently needed or require specialized skills to be used/replaced. The need and the quantity of these items should be assessed by technical staff before procuring the main medical devices, and procured together. It is recommended to store and use them in central and local maintenance department. Primary valve assembly, regulator valve assembly, pressure safety valve, inlet/outlet connectors, full set of sealings, integral valve assembly, manometer and flowmeter (for integral valves).
Mobility, portability (if relevant) | Portable or stationary (depending on the size of the cylinder).
Documentation requirements (English language mandatory) | Set: user and maintenance manuals, hard and soft copies, in English (mandatory) and other languages (preferable). Certificate of calibration and inspection. Troubleshooting, calibration and routine maintenance. List of all spare parts and accessories, with part numbers and contact details for parts supply. Document with contact details of manufacturer, supplier and local service agent.
Transportation and storage and primary packaging labelling | Applicable regulations on transport and storage of cylinders may vary if the cylinders are empty or partially/fully filled. Compliant with regulations on hazardous goods, flammable, explosive, compressed gas, according with GHS and international standards is mandatory. Sealed container. Capable of being transported and stored in ambient temperature of at least 5–50 °C, relative humidity of at least 15–95% non-condensing. Specific requirements for altitude may be required, depending on the installation site. Hazardous goods, flammable, explosive, compressed gas labelling according with GHS and international standards and regulations. Primary packaging: Unit of use: one (1) cylinder or valve/regulator in a box or case with manufacturer’s instruction for use, spare parts and accessories (when applicable). Cylinder type and content in litres, tare weight (weight when empty), maximum cylinder pressure, cylinder size code. Labelling on the primary packaging: Name and/or trademark of the manufacturer; manufacturer’s product reference; type of product and main characteristics; lot number prefixed by the word “LOT” (or equivalent harmonized symbol) (if applicable); information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonized symbol); information for handling, if applicable (or equivalent harmonized symbol). Over packaging: Packaging unit. Labelling on the packaging unit: Labelling to be the same as primary packaging. Extra information required: number of units.
Standards, for the manufacturer | Certified quality management system for medical devices (e.g. ISO 13485). General quality management (e.g. ISO 9001). Application of risk management to medical devices (e.g. ISO 14971).
Regulatory approval/ certification | Free sales certificate (FSC) or certificate for exportation of medical device provided by the authority in manufacturing country. Proof of regulatory compliance, as appropriate, per the product’s risk classification (e.g. Food and Drug Administration [FDA] and/or Conformité Européenne [CE]).
Standards, for product performance | Compliance to the following international standards or to regional or national equivalent (including the technical tests for safety and performance from accredited laboratory or third party) for: Colour coding ISO or ANSI for medical gases. Conforms to ISO, NFPA and/or CGA standards, and/or UL or CSA approved. ISO 11114 Gas cylinders – Compatibility of cylinder and valve materials with gas contents. ISO 10524 Pressure regulators for use with medical gases. ISO 15002 Flow-metering devices for connection to terminal units of medical gas pipeline systems. ISO 15245 Gas cylinders – Parallel threads for connection of valves to gas cylinders. ISO 10297 Gas cylinders – Cylinder valves – Specification and type testing. ISO 17871 Gas cylinders – Quick-release cylinder valves – Specification and type testing. ISO 17879 Gas cylinders – Self-closing cylinder valves – Specification and type testing. ISO 407 Small medical gas cylinders – Pin-index yoke-type valve connections. ISO 5145 Cylinder valve outlets for gases and gas mixtures – Selection and dimensioning. ISO 11117 Gas cylinders – Valve protection caps and valve guards – Design, construction and tests. ISO 11363 Gas cylinders – 17E and 25E taper threads for connection of valves to gas cylinders. ISO 12209 Gas cylinders – Outlet connections for gas cylinder valves for compressed breathable air. ISO 14246 Gas cylinders – Cylinder valves – Manufacturing tests and examinations. ISO 22435 Gas cylinders – Cylinder valves with integrated pressure regulators. ISO 7866 Gas cylinders – Refillable seamless aluminium alloy gas cylinders – Design, construction and testing. ISO 20701 Gas cylinders – Refillable welded aluminium-alloy cylinders – Design, construction and testing. ISO 9809 Gas cylinders – Refillable seamless steel gas cylinders – Design, construction and testing. ISO 11119 Gas cylinders – Refillable composite gas cylinders and tubes – Design, construction and testing. ISO 13341 Gas cylinders – Fitting of valves to gas cylinders. ISO 32 Gas cylinders for medical use – Marking for identification of content. ISO 7225 Gas cylinders – Precautionary labels. ISO 10461 Gas cylinders – Seamless aluminium-alloy gas cylinders – Periodic inspection and testing. ISO 11623 Gas cylinders – Composite construction – Periodic inspection and testing. ISO 15223-1 Medical devices – Symbols to be used with medical device labels, labelling and information to be supplied – Part 1: General requirements. ISO 15996 Gas cylinders – Residual pressure valves – Specification and type testing of cylinder valves incorporating residual pressure devices. ISO 15001 Anaesthetic and respiratory equipment – Compatibility with oxygen.
Warranty | 5 years recommended for the cylinders, 3 years recommended for the pressure regulators and valves (2 years at least).